## Conduit Fill
Conduit Fill Calculator based on the NEC Chapter 9, Tables 4 and 5, by Lorn J. MacIlravie, Version 9-25-2019 2244
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | TYPE | COL.
LINE | QTY | SIZE | TYPE | IN2 FROM TABLE 5 | TOTAL AREA | [5 empty] | WIRE | RFH-2, FFH-2, RFHH-2 | RHH, RHW, RHW-2 | SF-2, SFF-2 | SF-1, SFF-1 | RFH-1, TF, TFF, XF, XFF | TF, TFF, XF, XFF | TW, XF, XFF, THHW, THW, THW-2 | TW, THHW, THW, THW-2 | RHH*, RHW*, RHW-2* | RHH*, RHW*, RHW-2*, XF, XFF | RHH*, RHW*, RHW-2* | TW, THW, THHW, THW-2, RHH*, RHW*, RHW-2* | TFN, TFFN | THHN, THWN, THWN-2 | PF, PGFF, PGF, PFF, PTF, PAF, PTFF, PAFF | PF, PGFF, PGF, PFF, PTF, PAF, PTFF, PAFF, TFE, FEP, PFA, PFA, FEPB, PFAH | TFE, FEP, PFA, FEPD, PFAH | TFE, PFAH, PFA | TFE, PFA, PFAH, Z | ZF, ZFF, ZHF | Z, ZF, ZFF, ZHF | Z | XHHW, XHHW-2, XHH | KF-2, KFF-2 | KF-1, KFF1 | CABLE | WIRE | 1 | LINE | SIZE | TYPE | COL. | AREA
1 | 2 | # 14 | THHN, THWN, THWN-2 | 0.0097 | 0.0194 | [5 empty] | # 18 | 0.0145 | 0 | 0.0115 | 0.0065 | 0.0088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0055 | 0 | 0.0058 | 0 | 0 | 0 | 0 | 0.0045 | 0 | 0 | 0 | 0.003 | 0.0026 | 0 | RFH-2, FFH-2, RFHH-2 | 2 | 1 | # 14 | THHN, THWN, THWN-2 | 15 | 0.0097
2 | 2 | # 6 | THHN, THWN, THWN-2 | 0.0507 | 0.1014 | [5 empty] | # 16 | 0.0172 | 0 | 0.0139 | 0 | 0 | 0.0109 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0072 | 0 | 0.0075 | 0 | 0 | 0 | 0 | 0.0061 | 0 | 0 | 0 | 0.0043 | 0.0037 | 0 | RHH, RHW, RHW-2 | 3 | 2 | # 6 | THHN, THWN, THWN-2 | 15 | 0.0507
3 | 0 | # 4 | XHHW, XHHW-2, XHH | 0.0814 | 0 | [5 empty] | # 14 | 0 | 0.0293 | 0.0172 | 0 | 0 | 0 | 0.0139 | 0 | 0.0209 | 0 | 0 | 0.0139 | 0 | 0.0097 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0.0083 | 0 | 0.139 | 0.0064 | 0.0055 | 0 | SF-2, SFF-2 | 4 | 3 | # 4 | XHHW, XHHW-2, XHH | 24 | 0.0814
4 | 0 | 2/O | THHN, THWN, THWN-2 | 0.2223 | 0 | [5 empty] | # 12 | 0 | 0.0353 | 0 | 0 | 0 | 0 | 0 | 0.0181 | 0 | 0.026 | 0 | 0.0181 | 0 | 0.0133 | 0 | 0 | 0.0137 | 0 | 0 | 0 | 0 | 0.0117 | 0.0181 | 0.0092 | 0.0083 | 0 | SF-1, SFF-1 | 5 | 4 | 2/O | THHN, THWN, THWN-2 | 15 | 0.2223
5 | 0 | 4/O | RHH, RHW, RHW-2 | 0.4754 | 0 | [5 empty] | # 10 | 0 | 0.0437 | 0 | 0 | 0 | 0 | 0 | 0.0243 | 0 | 0.0333 | 0 | 0.0243 | 0 | 0.0211 | 0 | 0 | 0.0191 | 0 | 0 | 0 | 0 | 0.0191 | 0.0243 | 0.0139 | 0.0127 | 0 | RFH-1, TF, TFF, XF, XFF | 6 | 5 | 4/O | RHH, RHW, RHW-2 | 3 | 0.4754
6 | 0 | 250 kcmil | RHH, RHW, RHW-2 | 0.6291 | 0 | [5 empty] | # 8 | 0 | 0.0853 | 0 | 0 | 0 | 0 | 0 | 0.0437 | 0 | 0 | 0.0556 | 0.0437 | 0 | 0.0366 | 0 | 0 | 0.0333 | 0 | 0 | 0 | 0 | 0.0302 | 0.0437 | 0 | 0 | 0 | TF, TFF, XF, XFF | 7 | 6 | 250 kcmil | RHH, RHW, RHW-2 | 3 | 0.6291
7 | 0 | 350 kcmil | THHN, THWN, THWN-2 | 0.5242 | 0 | [5 empty] | # 6 | 0 | 0.1041 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0726 | 0 | 0.0507 | 0 | 0 | 0.0468 | 0 | 0 | 0 | 0 | 0.043 | 0.059 | 0 | 0 | 0 | TW, XF, XFF, THHW, THW, THW-2 | 8 | 7 | 350 kcmil | THHN, THWN, THWN-2 | 15 | 0.5242
8 | 0 | # 14 | THHN, THWN, THWN-2 | 0.0097 | 0 | [5 empty] | # 4 | 0 | 0.1333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0973 | 0 | 0.0824 | 0 | 0 | 0.067 | 0 | 0 | 0 | 0 | 0.0625 | 0.0814 | 0 | 0 | 0 | TW, THHW, THW, THW-2 | 9 | 8 | # 14 | THHN, THWN, THWN-2 | 15 | 0.0097
9 | 0 | # 12 | THHN, THWN, THWN-2 | 0.0133 | 0 | [5 empty] | # 3 | 0 | 0.1521 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1134 | 0 | 0.0973 | 0 | 0 | 0.0804 | 0 | 0 | 0 | 0 | 0.0855 | 0.0962 | 0 | 0 | 0 | RHH*, RHW*, RHW-2* | 10 | 9 | # 12 | THHN, THWN, THWN-2 | 15 | 0.0133
10 | 0 | 0.25" | CABLE | 0.049087 | 0 | [5 empty] | # 2 | 0 | 0.175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1333 | 0 | 0.1158 | 0 | 0 | 0.0973 | 0 | 0 | 0 | 0 | 0.1029 | 0.1146 | 0 | 0 | 0 | RHH*, RHW*, RHW-2*, XF, XFF | 11 | 10 | 0.25" | CABLE | 27 | 0.049087
11 | 0 | 0.1875" | CABLE | 0.027612 | 0 | [5 empty] | # 1 | 0 | 0.266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1901 | 0 | 0.1562 | 0 | 0 | 0 | 0.1399 | 0 | 0 | 0 | 0.1269 | 0.1534 | 0 | 0 | 0 | RHH*, RHW*, RHW-2* | 12 | 11 | 0.1875" | CABLE | 27 | 0.027612
12 | 0 | 1.5" | CABLE | 1.7671 | 0 | [5 empty] | 1/O | 0 | 0.3039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2223 | 0 | 0.1855 | 0 | 0 | 0 | 0 | 0.1676 | 0 | 0 | 0 | 0.1825 | 0 | 0 | 0 | TW, THW, THHW, THW-2, RHH*, RHW*, RHW-2* | 13 | 12 | 1.5" | CABLE | 27 | 1.7671
13 | 0 | # 10 | XHHW, XHHW-2, XHH | 0.0243 | 0 | [5 empty] | 2/O | 0 | 0.3505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2624 | 0 | 0.2223 | 0 | 0 | 0 | 0 | 0.2027 | 0 | 0 | 0 | 0.219 | 0 | 0 | 0 | TFN, TFFN | 14 | 13 | # 10 | XHHW, XHHW-2, XHH | 24 | 0.0243
14 | 0 | # 10 | XHHW, XHHW-2, XHH | 0.0243 | 0 | [5 empty] | 3/O | 0 | 0.4072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3117 | 0 | 0.2679 | 0 | 0 | 0 | 0 | 0.2463 | 0 | 0 | 0 | 0.2642 | 0 | 0 | 0 | THHN, THWN, THWN-2 | 15 | 14 | # 10 | XHHW, XHHW-2, XHH | 24 | 0.0243
15 | 0 | # 10 | XHHW, XHHW-2, XHH | 0.0243 | 0 | [5 empty] | 4/O | 0 | 0.4754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3718 | 0 | 0.3237 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0.3197 | 0 | 0 | 0 | PF, PGFF, PGF, PFF, PTF, PAF, PTFF, PAFF | 16 | 15 | # 10 | XHHW, XHHW-2, XHH | 24 | 0.0243
| 4 | Number of conductors and / or cables |  |  | 0.1208 | Total Calculated Wire Fill |  |  |  |  | 250 kcmil | 0 | 0.6291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4596 | 0 | 0.397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3904 | 0 | 0 | 0 | PF, PGFF, PGF, PFF, PTF, PAF, PTFF, PAFF, TFE, FEP, PFA, PFA, FEPB, PFAH | 17
[5 empty] | 1.15 | Optional Multiplier for Spare Space |  |  |  |  | 300 kcmil | 0 | 0.7088 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5281 | 0 | 0.4608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4536 | 0 | 0 | 0 | TFE, FEP, PFA, FEPD, PFAH | 18
[5 empty] | 0.13892 | Total Wire Fill after Multiplier |  |  |  |  | 350 kcmil | 0 | 0.787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5958 | 0 | 0.5242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5166 | 0 | 0 | 0 | TFE, PFAH, PFA | 19
[11 empty] | 400 kcmil | 0 | 0.8626 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6619 | 0 | 0.5863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5782 | 0 | 0 | 0 | TFE, PFA, PFAH, Z | 20
EMT | EMT - Electrical Metallic tubing - Article 358 | [7 empty] | Decimal Conversion |  | 500 kcmil | 0 | 1.0082 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7901 | 0 | 0.7073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6984 | 0 | 0 | 0 | ZF, ZFF, ZHF | 21
| TRADE | OVER 2 WIRES | < 24" Nipple | 1 WIRE | 2 WIRES | TOTAL AREA | SEAL OFF | TRADE | 1/16" | 0.0625" | 600 kcmil | 0 | 1.2135 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9729 | 0 | 0.8676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8709 | 0 | 0 | 0 | Z, ZF, ZFF, ZHF | 22
| SIZE | 40% | 60% | 53% | 31% | 100% | 25% | SIZE | 1/8" | 0.125" | 700 kcmil | 0 | 1.3561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.101 | 0 | 0.9887 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9923 | 0 | 0 | 0 | Z | 23
| 1/2" | 0.1216 | 0.1824 | 0.16112 | 0.09424 | 0.304 | 0.076 | 1/2" | 3/16" | 0.1875" | 750 kcmil | 0 | 1.4272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1652 | 0 | 1.0496 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0532 | 0 | 0 | 0 | XHHW, XHHW-2, XHH | 24
| 3/4" | 0.2132 | 0.3198 | 0.28249 | 0.16523 | 0.533 | 0.13325 | 3/4" | 1/4" | 0.25" | 800 kcmil | 0 | 1.4957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2272 | 0 | 1.1085 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1122 | 0 | 0 | 0 | KF-2, KFF-2 | 25
| 1" | 0.3456 | 0.5184 | 0.45792 | 0.26784 | 0.864 | 0.216 | 1" | 5/16" | 0.3125" | 900 kcmil | 0 | 1.6377 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3561 | 0 | 1.2311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2351 | 0 | 0 | 0 | KF-1, KFF1 | 26
| 1 - 1/4" | 0.5984 | 0.8976 | 0.79288 | 0.46376 | 1.496 | 0.374 | 1 - 1/4" | 3/8" | 0.375" | 1000 kcmil | 0 | 1.7719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4784 | 0 | 1.3478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3519 | 0 | 0 | 0 | CABLE | 27
| 1 - 1/2" | 0.8144 | 1.2216 | 1.0791 | 0.63116 | 2.036 | 0.509 | 1 - 1/2" | 7/16" | 0.4375" | 1250 kcmil | 0 | 2.3479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.718 | 0 | 0 | 0
| 2" | 1.3424 | 2.0136 | 1.7787 | 1.0404 | 3.356 | 0.839 | 2" | 1/2" | 0.5" | 1500 kcmil | 0 | 2.6938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.1695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0156 | 0 | 0 | 0
| 2 - 1/2" | 2.3432 | 3.5148 | 3.1047 | 1.816 | 5.858 | 1.4645 | 2 - 1/2" | 9/16" | 0.5625" | 1750 kcmil | 0 | 3.0357 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4773 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3127 | 0 | 0 | 0
| 3" | 3.5384 | 5.3076 | 4.6884 | 2.7423 | 8.846 | 2.2115 | 3" | 5/8" | 0.625" | 2000 kcmil | 0 | 3.3719 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6073 | 0 | 0 | 0
| 3 - 1/2" | 4.618 | 6.927 | 6.1189 | 3.5789 | 11.545 | 2.8862 | 3 - 1/2" | 11/16" | 0.6875" | 0.0625" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.003068
| 4" | 5.9012 | 8.8518 | 7.8191 | 4.5734 | 14.753 | 3.6883 | 4" | 3/4" | 0.75" | 0.125" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.012272
[9 empty] | 13/16" | 0.8125" | 0.1875" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.027612
ENT | ENT - Electrical Nonmetallic Tubing - Article 362 | [7 empty] | 7/8" | 0.875" | 0.25" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.049087
| TRADE | OVER 2 WIRES | < 24" Nipple | 1 WIRE | 2 WIRES | TOTAL AREA | SEAL OFF | TRADE | 15/16" | 0.9375" | 0.3125" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.076699
| SIZE | 40% | 60% | 53% | 31% | 100% | 25% | SIZE | 1" | 1" | 0.375" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.11045
| 1/2" | 0.114 | 0.171 | 0.15105 | 0.08835 | 0.285 | 0.07125 | 1/2" | 1-1/16" | 1.0625" | 0.4375" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.15033
| 3/4" | 0.2032 | 0.3048 | 0.26924 | 0.15748 | 0.508 | 0.127 | 3/4" | 1-1/8" | 1.125" | 0.5" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19635
| 1" | 0.3328 | 0.4992 | 0.44096 | 0.25792 | 0.832 | 0.208 | 1" | 1-3/16" | 1.1875" | 0.5625" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2485
| 1 - 1/4" | 0.5812 | 0.8718 | 0.77009 | 0.45043 | 1.453 | 0.36325 | 1 - 1/4" | 1-1/4" | 1.25" | 0.625" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3068
| 1 - 1/2" | 0.7944 | 1.1916 | 1.0526 | 0.61566 | 1.986 | 0.4965 | 1 - 1/2" | 1-5/16" | 1.3125" | 0.6875" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.37122
| 2" | 1.3164 | 1.9746 | 1.7442 | 1.0202 | 3.291 | 0.82275 | 2" | 1-3/8" | 1.375" | 0.75" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44179
| 2 - 1/2" | - | - | - | - | - | - | 2 - 1/2" | 1-7/16" | 1.4375" | 0.8125" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.51849
| 3" | - | - | - | - | - | - | 3" | 1-1/2" | 1.5" | 0.875" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.60132
| 3 - 1/2" | - | - | - | - | - | - | 3 - 1/2" | 1-9/16" | 1.5625" | 0.9375" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.69029
[9 empty] | 1-5/8" | 1.625" | 1" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.7854
FMC | FMC - Flexible Metal Conduit - Article 348 | [7 empty] | 1-11/16" | 1.6875" | 1.0625" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.88664
| TRADE | OVER 2 WIRES | < 24" Nipple | 1 WIRE | 2 WIRES | TOTAL AREA | SEAL OFF | TRADE | 1-3/4" | 1.75" | 1.125" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99402
| SIZE | 40% | 60% | 53% | 31% | 100% | 25% | SIZE | 1-13/16" | 1.8125" | 1.1875" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1075
| 3/8" | 0.0464 | 0.0696 | 0.06148 | 0.03596 | 0.116 | 0.029 | 3/8" | 1-7/8" | 1.875" | 1.25" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2272
| 1/2" | 0.1268 | 0.1902 | 0.16801 | 0.09827 | 0.317 | 0.07925 | 1/2" | 1-15/16" | 1.9375" | 1.3125" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.353
| 3/4" | 0.2132 | 0.3198 | 0.28249 | 0.16523 | 0.533 | 0.13325 | 3/4" | 2" | 2" | 1.375" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.4849
| 1" | 0.3268 | 0.4902 | 0.43301 | 0.25327 | 0.817 | 0.20425 | 1" | 2-1/16" | 2.0625" | 1.4375" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.623
| 1 - 1/4" | 0.5108 | 0.7662 | 0.67681 | 0.39587 | 1.277 | 0.31925 | 1 - 1/4" | 2-1/8" | 2.125" | 1.5" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.7671
| 1 - 1/2" | 0.7432 | 1.1148 | 0.98474 | 0.57598 | 1.858 | 0.4645 | 1 - 1/2" | 2-3/16" | 2.1875" | 1.5625" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9175
| 2" | 1.3076 | 1.9614 | 1.7326 | 1.0134 | 3.269 | 0.81725 | 2" | 2-1/4" | 2.25" | 1.625" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0739
| 2 - 1/2" | 1.9636 | 2.9454 | 2.6018 | 1.5218 | 4.909 | 1.2272 | 2 - 1/2" | 2-5/16" | 2.3125" | 1.6875" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2365
| 3" | 2.8276 | 4.2414 | 3.7466 | 2.1914 | 7.069 | 1.7672 | 3" | 2-3/8" | 2.375" | 1.75" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4053
| 3 - 1/2" | 3.8484 | 5.7726 | 5.0991 | 2.9825 | 9.621 | 2.4053 | 3 - 1/2" | 2-7/16" | 2.4375" | 1.8125" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5802
| 4" | 5.0264 | 7.5396 | 6.66 | 3.8955 | 12.566 | 3.1415 | 4" | 2-1/2" | 2.5" | 1.875" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7612
[9 empty] | 2-9/16" | 2.5625" | 1.9375" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9483
IMC | IMC - Intermediate Metal Conduit - Article 342 | [7 empty] | 2-5/8" | 2.625" | 2" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1416
| TRADE | OVER 2 WIRES | < 24" Nipple | 1 WIRE | 2 WIRES | TOTAL AREA | SEAL OFF | TRADE | 2-11/16" | 2.6875" | 2.0625" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.341
| SIZE | 40% | 60% | 53% | 31% | 100% | 25% | SIZE | 2-3/4" | 2.75" | 2.125" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5466
| 3/8" | - | - | - | - | - | - | 3/8" | 2-13/16" | 2.8125" | 2.1875" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.7583
| 1/2" | 0.1368 | 0.2052 | 0.18126 | 0.10602 | 0.342 | 0.0855 | 1/2" | 2-7/8" | 2.875" | 2.25" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9761
| 3/4" | 0.2344 | 0.3516 | 0.31058 | 0.18166 | 0.586 | 0.1465 | 3/4" | 2-15/16" | 2.9375" | 2.3125" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.2
| 1" | 0.3836 | 0.5754 | 0.50827 | 0.29729 | 0.959 | 0.23975 | 1" | 3" | 3" | 2.375" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4301
| 1 - 1/4" | 0.6588 | 0.9882 | 0.87291 | 0.51057 | 1.647 | 0.41175 | 1 - 1/4" | 3-1/16" | 3.0625" | 2.4375" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.6664
| 1 - 1/2" | 0.89 | 1.335 | 1.1792 | 0.68975 | 2.225 | 0.55625 | 1 - 1/2" | 3-1/8" | 3.125" | 2.5" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.9087
| 2" | 1.452 | 2.178 | 1.9239 | 1.1253 | 3.63 | 0.9075 | 2" | 3-3/16" | 3.1875" | 2.5625" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.1572
| 2 - 1/2" | 2.054 | 3.081 | 2.7216 | 1.5918 | 5.135 | 1.2837 | 2 - 1/2" | 3-1/4" | 3.25" | 2.625" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4119
| 3" | 3.1688 | 4.7532 | 4.1987 | 2.4558 | 7.922 | 1.9805 | 3" | 3-5/16" | 3.3125" | 2.6875" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6727
| 3 - 1/2" | 4.2336 | 6.3504 | 5.6095 | 3.281 | 10.584 | 2.646 | 3 - 1/2" | 3-3/8" | 3.375" | 2.75" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.9396
| 4" | 5.4524 | 8.1786 | 7.2244 | 4.2256 | 13.631 | 3.4078 | 4" | 3-7/16" | 3.4375" | 2.8125" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.2126
[9 empty] | 3-1/2" | 3.5" | 2.875" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4918
LFNC-A* | LFNC-A* - Liquidtight Flexible Nonmetallic Conduit- Article 356 | [9 empty] | 2.9375" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7771
| TRADE | OVER 2 WIRES | < 24" Nipple | 1 WIRE | 2 WIRES | TOTAL AREA | SEAL OFF | TRADE |  |  | 3" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.0686
| SIZE | 40% | 60% | 53% | 31% | 100% | 25% | SIZE |  |  | 3.0625" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3662
| 3/8" | 0.0768 | 0.1152 | 0.10176 | 0.05952 | 0.192 | 0.048 | 3/8" |  |  | 3.125" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6699
| 1/2" | 0.1248 | 0.1872 | 0.16536 | 0.09672 | 0.312 | 0.078 | 1/2" |  |  | 3.1875" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.9798
| 3/4" | 0.214 | 0.321 | 0.28355 | 0.16585 | 0.535 | 0.13375 | 3/4" |  |  | 3.25" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.2958
| 1" | 0.3416 | 0.5124 | 0.45262 | 0.26474 | 0.854 | 0.2135 | 1" |  |  | 3.3125" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6179
| 1 - 1/4" | 0.6008 | 0.9012 | 0.79606 | 0.46562 | 1.502 | 0.3755 | 1 - 1/4" |  |  | 3.375" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9462
| 1 - 1/2" | 0.8072 | 1.2108 | 1.0695 | 0.62558 | 2.018 | 0.5045 | 1 - 1/2" |  |  | 3.4375" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2806
| 2" | 1.3372 | 2.0058 | 1.7718 | 1.0363 | 3.343 | 0.83575 | 2" |  |  | 3.5" | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.6211
LFNC-B* | LFNC-B* - Liquidtight Flexible Nonmetallic Conduit- Article 356
| TRADE | OVER 2 WIRES | < 24" Nipple | 1 WIRE | 2 WIRES | TOTAL AREA | SEAL OFF | TRADE
| SIZE | 40% | 60% | 53% | 31% | 100% | 25% | SIZE
| 3/8" | 0.0768 | 0.1152 | 0.10176 | 0.05952 | 0.192 | 0.048 | 3/8"
| 1/2" | 0.1256 | 0.1884 | 0.16642 | 0.09734 | 0.314 | 0.0785 | 1/2"
| 3/4" | 0.2164 | 0.3246 | 0.28673 | 0.16771 | 0.541 | 0.13525 | 3/4"
| 1" | 0.3492 | 0.5238 | 0.46269 | 0.27063 | 0.873 | 0.21825 | 1"
| 1 - 1/4" | 0.6112 | 0.9168 | 0.80984 | 0.47368 | 1.528 | 0.382 | 1 - 1/4"
| 1 - 1/2" | 0.7924 | 1.1886 | 1.0499 | 0.61411 | 1.981 | 0.49525 | 1 - 1/2"
| 2" | 1.2984 | 1.9476 | 1.7204 | 1.0063 | 3.246 | 0.8115 | 2"
LFNC-C* | LFNC-C* - Liquidtight Flexible Nonmetallic Conduit- Article 356
| TRADE | OVER 2 WIRES | < 24" Nipple | 1 WIRE | 2 WIRES | TOTAL AREA | SEAL OFF | TRADE
| SIZE | 40% | 60% | 53% | 31% | 100% | 25% | SIZE
| 3/8" | 0.074 | 0.111 | 0.09805 | 0.05735 | 0.185 | 0.04625 | 3/8"
| 1/2" | 0.1208 | 0.1812 | 0.16006 | 0.09362 | 0.302 | 0.0755 | 1/2"
| 3/4" | 0.2088 | 0.3132 | 0.27666 | 0.16182 | 0.522 | 0.1305 | 3/4"
| 1" | 0.3332 | 0.4998 | 0.44149 | 0.25823 | 0.833 | 0.20825 | 1"
| 1 - 1/4" | 0.5896 | 0.8844 | 0.78122 | 0.45694 | 1.474 | 0.3685 | 1 - 1/4"
| 1 - 1/2" | 0.7892 | 1.1838 | 1.0457 | 0.61163 | 1.973 | 0.49325 | 1 - 1/2"
| 2" | 1.314 | 1.971 | 1.741 | 1.0184 | 3.285 | 0.82125 | 2"
LFMC | LFMC - Liquidtight Flexible Metal Conduit - Article 350
| TRADE | OVER 2 WIRES | < 24" Nipple | 1 WIRE | 2 WIRES | TOTAL AREA | SEAL OFF | TRADE
| SIZE | 40% | 60% | 53% | 31% | 100% | 25% | SIZE
| 3/8" | 0.0768 | 0.1152 | 0.10176 | 0.05952 | 0.192 | 0.048 | 3/8"
| 1/2" | 0.1256 | 0.1884 | 0.16642 | 0.09734 | 0.314 | 0.0785 | 1/2"
| 3/4" | 0.2164 | 0.3246 | 0.28673 | 0.16771 | 0.541 | 0.13525 | 3/4"
| 1" | 0.3492 | 0.5238 | 0.46269 | 0.27063 | 0.873 | 0.21825 | 1"
| 1 - 1/4" | 0.6112 | 0.9168 | 0.80984 | 0.47368 | 1.528 | 0.382 | 1 - 1/4"
| 1 - 1/2" | 0.7924 | 1.1886 | 1.0499 | 0.61411 | 1.981 | 0.49525 | 1 - 1/2"
| 2" | 1.2984 | 1.9476 | 1.7204 | 1.0063 | 3.246 | 0.8115 | 2"
| 2 - 1/2" | 1.9524 | 2.9286 | 2.5869 | 1.5131 | 4.881 | 1.2203 | 2 - 1/2"
| 3" | 2.99 | 4.485 | 3.9617 | 2.3173 | 7.475 | 1.8687 | 3"
| 3 - 1/2" | 3.8924 | 5.8386 | 5.1574 | 3.0166 | 9.731 | 2.4327 | 3 - 1/2"
| 4" | 5.0768 | 7.6152 | 6.7268 | 3.9345 | 12.692 | 3.173 | 4"
| 5" | - | - | - | - | - | - | 5"
| 6" | - | - | - | - | - | - | 6"
RMC | RMC - Rigid Metal Conduit - Article 344
| TRADE | OVER 2 WIRES | < 24" Nipple | 1 WIRE | 2 WIRES | TOTAL AREA | SEAL OFF | TRADE
| SIZE | 40% | 60% | 53% | 31% | 100% | 25% | SIZE
| 3/8" | - | - | - | - | - | - | 3/8"
| 1/2" | 0.1256 | 0.1884 | 0.16642 | 0.09734 | 0.314 | 0.0785 | 1/2"
| 3/4" | 0.2196 | 0.3294 | 0.29097 | 0.17019 | 0.549 | 0.13725 | 3/4"
| 1" | 0.3548 | 0.5322 | 0.47011 | 0.27497 | 0.887 | 0.22175 | 1"
| 1 - 1/4" | 0.6104 | 0.9156 | 0.80878 | 0.47306 | 1.526 | 0.3815 | 1 - 1/4"
| 1 - 1/2" | 0.8284 | 1.2426 | 1.0976 | 0.64201 | 2.071 | 0.51775 | 1 - 1/2"
| 2" | 1.3632 | 2.0448 | 1.8062 | 1.0565 | 3.408 | 0.852 | 2"
| 2 - 1/2" | 1.9464 | 2.9196 | 2.579 | 1.5085 | 4.866 | 1.2165 | 2 - 1/2"
| 3" | 2.9996 | 4.4994 | 3.9745 | 2.3247 | 7.499 | 1.8747 | 3"
| 3 - 1/2" | 4.004 | 6.006 | 5.3053 | 3.1031 | 10.01 | 2.5025 | 3 - 1/2"
| 4" | 5.1528 | 7.7292 | 6.8275 | 3.9934 | 12.882 | 3.2205 | 4"
| 5" | 8.0848 | 12.1272 | 10.7124 | 6.2657 | 20.212 | 5.053 | 5"
| 6" | 11.6632 | 17.4948 | 15.4537 | 9.039 | 29.158 | 7.2895 | 6"
PVC Sch. 80 | PVC Sch. 80 - Rigid PVC Conduit - Article 352
| TRADE | OVER 2 WIRES | < 24" Nipple | 1 WIRE | 2 WIRES | TOTAL AREA | SEAL OFF | TRADE
| SIZE | 40% | 60% | 53% | 31% | 100% | 25% | SIZE
| 3/8" | - | - | - | - | - | - | 3/8"
| 1/2" | 0.0868 | 0.1302 | 0.11501 | 0.06727 | 0.217 | 0.05425 | 1/2"
| 3/4" | 0.1636 | 0.2454 | 0.21677 | 0.12679 | 0.409 | 0.10225 | 3/4"
| 1" | 0.2752 | 0.4128 | 0.36464 | 0.21328 | 0.688 | 0.172 | 1"
| 1 - 1/4" | 0.4948 | 0.7422 | 0.65561 | 0.38347 | 1.237 | 0.30925 | 1 - 1/4"
| 1 - 1/2" | 0.6844 | 1.0266 | 0.90683 | 0.53041 | 1.711 | 0.42775 | 1 - 1/2"
| 2" | 1.1496 | 1.7244 | 1.5232 | 0.89094 | 2.874 | 0.7185 | 2"
| 2 - 1/2" | 1.6476 | 2.4714 | 2.1831 | 1.2769 | 4.119 | 1.0297 | 2 - 1/2"
| 3" | 2.5768 | 3.8652 | 3.4143 | 1.997 | 6.442 | 1.6105 | 3"
| 3 - 1/2" | 3.4752 | 5.2128 | 4.6046 | 2.6933 | 8.688 | 2.172 | 3 - 1/2"
| 4" | 4.5032 | 6.7548 | 5.9667 | 3.49 | 11.258 | 2.8145 | 4"
| 5" | 7.142 | 10.713 | 9.4632 | 5.5351 | 17.855 | 4.4638 | 5"
| 6" | 10.2392 | 15.3588 | 13.5669 | 7.9354 | 25.598 | 6.3995 | 6"
PVC Sch. 40 | PVC Sch. 40 - Rigid PVC Conduit and HDPE Conduit - Article 352 and 353
| TRADE | OVER 2 WIRES | < 24" Nipple | 1 WIRE | 2 WIRES | TOTAL AREA | SEAL OFF | TRADE
| SIZE | 40% | 60% | 53% | 31% | 100% | 25% | SIZE
| 3/8" | - | - | - | - | - | - | 3/8"
| 1/2" | 0.114 | 0.171 | 0.15105 | 0.08835 | 0.285 | 0.07125 | 1/2"
| 3/4" | 0.2032 | 0.3048 | 0.26924 | 0.15748 | 0.508 | 0.127 | 3/4"
| 1" | 0.3328 | 0.4992 | 0.44096 | 0.25792 | 0.832 | 0.208 | 1"
| 1 - 1/4" | 0.5812 | 0.8718 | 0.77009 | 0.45043 | 1.453 | 0.36325 | 1 - 1/4"
| 1 - 1/2" | 0.7944 | 1.1916 | 1.0526 | 0.61566 | 1.986 | 0.4965 | 1 - 1/2"
| 2" | 1.3164 | 1.9746 | 1.7442 | 1.0202 | 3.291 | 0.82275 | 2"
| 2 - 1/2" | 1.878 | 2.817 | 2.4884 | 1.4554 | 4.695 | 1.1738 | 2 - 1/2"
| 3" | 2.9072 | 4.3608 | 3.852 | 2.2531 | 7.268 | 1.817 | 3"
| 3 - 1/2" | 3.8948 | 5.8422 | 5.1606 | 3.0185 | 9.737 | 2.4343 | 3 - 1/2"
| 4" | 5.0216 | 7.5324 | 6.6536 | 3.8917 | 12.554 | 3.1385 | 4"
| 5" | 7.9044 | 11.8566 | 10.4733 | 6.1259 | 19.761 | 4.9402 | 5"
| 6" | 11.4268 | 17.1402 | 15.1405 | 8.8558 | 28.567 | 7.1418 | 6"
PVC Type A | PVC Type A - Type A, Rigid PVC Conduit - Article 352
| TRADE | OVER 2 WIRES | < 24" Nipple | 1 WIRE | 2 WIRES | TOTAL AREA | SEAL OFF | TRADE
| SIZE | 40% | 60% | 53% | 31% | 100% | 25% | SIZE
| 1/2" | 0.154 | 0.231 | 0.20405 | 0.11935 | 0.385 | 0.09625 | 1/2"
| 3/4" | 0.26 | 0.39 | 0.3445 | 0.2015 | 0.65 | 0.1625 | 3/4"
| 1" | 0.4336 | 0.6504 | 0.57452 | 0.33604 | 1.084 | 0.271 | 1"
| 1 - 1/4" | 0.7068 | 1.0602 | 0.93651 | 0.54777 | 1.767 | 0.44175 | 1 - 1/4"
| 1 - 1/2" | 0.9296 | 1.3944 | 1.2317 | 0.72044 | 2.324 | 0.581 | 1 - 1/2"
| 2" | 1.4588 | 2.1882 | 1.9329 | 1.1306 | 3.647 | 0.91175 | 2"
| 2 - 1/2" | 2.1812 | 3.2718 | 2.8901 | 1.6904 | 5.453 | 1.3633 | 2 - 1/2"
| 3" | 3.2776 | 4.9164 | 4.3428 | 2.5401 | 8.194 | 2.0485 | 3"
| 3 - 1/2" | 4.2776 | 6.4164 | 5.6678 | 3.3151 | 10.694 | 2.6735 | 3 - 1/2"
| 4" | 5.4892 | 8.2338 | 7.2732 | 4.2541 | 13.723 | 3.4308 | 4"
| 5" | - | - | - | - | - | - | 5"
| 6" | - | - | - | - | - | - | 6"
PVC Type EB | PVC Type EB - Type EB, Rigid PVC Conduit - Article 352
| TRADE | OVER 2 WIRES | < 24" Nipple | 1 WIRE | 2 WIRES | TOTAL AREA | SEAL OFF | TRADE
| SIZE | 40% | 60% | 53% | 31% | 100% | 25% | SIZE
| 1/2" | - | - | - | - | - | - | 1/2"
| 3/4" | - | - | - | - | - | - | 3/4"
| 1" | - | - | - | - | - | - | 1"
| 1 - 1/4" | - | - | - | - | - | - | 1 - 1/4"
| 1 - 1/2" | - | - | - | - | - | - | 1 - 1/2"
| 2" | 1.5496 | 2.3244 | 2.0532 | 1.2009 | 3.874 | 0.9685 | 2"
| 2 - 1/2" | - | - | - | - | - | - | 2 - 1/2"
| 3" | 3.4836 | 5.2254 | 4.6158 | 2.6998 | 8.709 | 2.1772 | 3"
| 3 - 1/2" | 4.546 | 6.819 | 6.0235 | 3.5231 | 11.365 | 2.8413 | 3 - 1/2"
| 4" | 5.7792 | 8.6688 | 7.6574 | 4.4789 | 14.448 | 3.612 | 4"
| 5" | 8.878 | 13.317 | 11.7634 | 6.8804 | 22.195 | 5.5488 | 5"
| 6" | 12.612 | 18.918 | 16.7109 | 9.7743 | 31.53 | 7.8825 | 6"
Derating for CCC Calculations
6 | Total Conductors
0 | 1 | 1-2
0.8 | 0.8 | 4-6
0 | 0.7 | 7-9
0 | 0.5 | 10-20
0 | 0.45 | 21-30
0 | 0.4 | 31-40
0 | 0.35 | 41 +
0.8 | Derating Value
Instructions:
1. You can change the values in the yellow cells. |  |  | The one doesn't do anything. |  |  | Total Conductors
2. Check the results in the tables with the green and red cells. The green cells show you which conduits you can use. | [5 empty] | 4
3. The red cells show the conduits that are too small.
4. If a value doesn't show up when you choose a size and a type of wire, it just isn't in the tables in NEC Chapter 9, Tables 4 and 5. | [5 empty] | No. of CCC?
5. If you choose a measurement, in inches, make sure you choose "CABLE" under "TYPE" so the sheet calculates the total area for you. | [5 empty] | 6
6. If you aren't sure which "TYPE" of conductor to use, choose "THHN, THWN, THWN-2". That will get you close.
7. The password for this sheet is "password", just in case you want to break it. | [5 empty] | Derating for 6 CCC
8. If you find a problem, please call me, text me, or email me. I want to fix it. | [5 empty] | 0.8
Spreadsheet by:
Lorn J. MacIlravie
lorn@lornmac.com
Mobile: 307-228-3906
www.lornmac.com
The YELLOW cells are not protected.
Last Modified 8/20/2019