## Sheet1
NFPA 70E Annex D Incident Energy and Arc Flash Boundary Calculation Methods
Enter your values in the YELLOW boxes.
[5 empty] | 0.05 | MVA | 50 | KVA
| Ralph Lee Calculation Method |  |  |  | 480 | Volts
[5 empty] | 3.5 | %Z
| Short Circuit Calculation |  |  |  | 1 | t, Clearing Time, Seconds
| Isc = {(MVA*(10^6))/(1.732*Volts)}*{100/%Z} |  |  |  | 18 | D, Distance from Arc Source, Inches
| 0.05 | MVA
| 480 | Volts |  |  | Doughty Neal Paper D.3 |  | (Use for 600 Volts or LESS)
| 3.5 | %Z
Energy in Open Air D.3.2b
| 1718.3548 | Isc, Amperes Short Circuit |  | D.2.3a | E=(5271*(D^-1.9593)*t)*((0.0016*(F^2))-(0.0076*F)+0.8938)
| Power of the Arc |  |  |  | 1.7184 | F, Bolted fault short-circuit current, kA
P=1.732*Volts*Isc*(10^-6)*(0.707^2)
| 0.71407 | MW |  | D.2.3b | 1 | t, Clearing Time, Seconds
[5 empty] | 18 | D, Distance from Arc Source, Inches
Distance to a 2nd Degree Burn
| Dc={2.65*[1.732*Isc*Volts*10^-6]*0.1}^0.5 |  |  |  | 16.2035 | cals/cm2 | D.3.2b
| 0.61528 | Dc, Distance in Feet |  | D.2.3c
Arc in a Cubic Box D.3.3b
| Distance to a 2nd Degree Burn (Alternative Method) |  |  |  | E=(1038.7*(D^-1.4738)*t)*((0.0093*(F^2))-(0.3453*(F))+5.975)
Dc=[53*MVA*t]^0.5
| 1.6279 | Dc (Alternative Method) |  | D.2.3d | 1.7184 | F, Bolted fault short-circuit current, kA
| Energy in Open Air D.2.4 |  | (Use for MORE than 600 Volts) |  | 1 | t, Clearing Time, Seconds
| E=(793*F*kV*t)/(D^2) |  |  |  | 18 | D, Distance from Arc Source, Inches
| 1.7184 | F, Bolted fault short-circuit current, kA |  |  | 79.3589 | cals/cm2 |  | D.3.3b
| 0.48 | kV, system phase to phase voltage, kV
| 1 | t, Clearing Time, Seconds
| 18 | D, Distance from Arc Source, Inches
| 2.0187 | cals/cm2 |  | D.2.4